## Slide 1: EPLA Overview Electric Power Load Analysis (EPLA) Revision of 12 February 2026
Dr. Norbert Doerry
http://doerry.org/norbert/MarineElectricalPowerSystems/index.htm
© 2026 by Norbert Doerry This work is licensed via: CC BY 4.0 (https://creativecommons.org/)

## Slide 2: Essential Questions
What is an Electric Power Load Analysis (EPLA) and what is it used for? | Understand
What are the different analytic techniques used in conducting an EPLA and used in conjunction with an EPLA? | Understand
What is a proxy load and how is it used in an EPLA and related analyses? | Understand
How does an EPLA evolve over a ship design? | Understand

## Slide 3: Introduction Electric Power Load Analysis (EPLA)
Tracks all electrical loads onboard the ship in a Load List
  Loads modeled directly, or
  Loads modeled as part of a Proxy Load
Models these loads to conduct analyses to determine required characteristics of the power system
  Required power (current) ratings (power system components)
Supports many related analyses and design
  Energy storage
  In-rush current
  Pulsed loads
  Quality of service (power reliability)
  Endurance fuel (fuel tank size)
  Annual fuel
T9070-A3-DPC-010/310-1
(DPC 310-1)
(formerly DDS 310-1)

## Slide 4: Load list Database of information about all the loads onboard the ship
Nomenclature
Ship Work Breakdown Structure (SWBS) code (3-digit) or other product breakdown structure identifier
Location on the ship (zone and/or compartment) (needed for zonal equipment and distribution system sizing)
Point(s) of connection to the power system (power panel, load center, switchboard). If more than one point of connection, indicate the primary and alternate connection (if applicable). (needed for zonal equipment and distribution system sizing)
Identification Plate (nameplate) rating (include units)
Connected load (kW)
Peak load (kW)
Power type (voltage, number of phases, frequency)
Cyclic and intermittent behavior
Power requirements during different operating modes
In-rush current demand (if applicable)
Pulsed load characteristics (if applicable)
Use during different ship operating conditions
Temperature dependence
Tolerance to power disruption (for QOS analysis)
Correlation with other loads (such as mutually exclusive loads)
Load shed priority (mission priority)
Reference to the source of data to enable traceability

## Slide 5: Load factor analysis
Traditional method for performing load analysis
  Determining the rating of generator sets
Works well if all individual loads are small relative to the demand power
Load factors assigned to each load for each operational condition and ambient condition
  Operating load is the load factor multiplied by the connected load
  Operating load represents an average value for a given time interval
    Minutes for most power system equipment sizing
    24 hours for endurance fuel calculations and annual fuel consumption calculations
  Equipment that is not online have a load factor of 0.
Demand power for the power system component for a given operational condition and ambient condition
  Sum of the operating loads for all loads plus margin and service life allowance

## Slide 6: Zonal load factor analysis Modification to the load factor method
Applicable if at least one load is not small compared to the demand power.
Zonal load factors are equal to or greater than load factors
  Account for loads being large
  Account for peak loads being greater than average loads
Zonal operating load is product of zonal load factor and connected load
Residual zonal power demand for a load is the peak load minus the zonal operating load
Zonal demand power is the sum of the zonal operating loads plus the largest residual zonal power demand plus margin and service life allowance
DPC 310-1

## Slide 7: Stochastic Analysis
Models each load as a function of independent random variables
  Random variables modeled as probability density functions (PDF)
Margin should be reduced
  Captured in the PDF
  Smaller (perhaps ¼ of that used for load factor analysis) margin accounts for “missing” loads
Service life allowance still applies
Use Monte Carlo Simulation to determine the demand power
Monte Carlo Simulation
Example PDFs
DPC 310-1

## Slide 8: Modeling and simulation load analysis
Useful when …
  Have large loads
  Have loads with unusual electrical characteristics
  Have loads requiring large amounts of rolling reserve
  Correlation of loads is complex and cannot otherwise be adequately modeled by other means
Typically employs quasi-steady state modeling
  Only concerned with dynamics slower than about 1 second.
Usually involves integrating individual load models
Requires development of use-cases
  Realistic and stressing
  Aligned with EPS-CONOPS, PS-CONOPS, etc.
  Aligned with operating conditions
Worst-case demand power across all simulations typically used
Should employ a rigorous Verification and Validation effort

## Slide 9: Demand factor analysis
Simple legacy method for determining
  Current rating of cables feeding load centers and power panels
  Current ratings of corresponding circuit breakers
Zonal load factor method and stochastic load analysis are preferred methods
Demand factor is obtained based on the sum of the connected loads expressed as current (for 450 V ac) or power for other voltages
DPC 310-1

## Slide 10: 24-hour average load
Calculated at total ship level to support
  Endurance fuel calculations
  Annual fuel calculations
Load factor analysis
  Load factor is kWh consumed in 24 hours divided by 24
Parametric equations may be used early when only have load factors for 100 °F ambient conditions for the purpose of determining generator set power ratings
  Legacy method, other methods preferred
  Should not be used in preliminary design or later
  Equation [1] for all ships except aircraft carriers and large deck amphibious assault ships.
  Equation [2] for aircraft carriers and large deck amphibious assault ships.
DPC 310-1

## Slide 11: Load flow and limiting load flow
Load flow analysis
  Determines voltages, power, and current at each node of a power system for a given operational condition and ambient condition.
    Steady state analysis
    Based on load properties from EPLA
  Useful for determining
    Bus-tie current rating
    Power distribution equipment rating
  Supports
    Voltage drop calculations
Limiting load flow
  Calculates an upper bound for power and currents without a detailed understanding of generator and load configurations
  Levels
    Simplest level: based only on generator set ratings
    Less conservative level: refines simplest level by incorporating power system topology
    Least conservative level: refines less conservative level by incorporating the impact of loads

## Slide 12: Energy storage capacity (power and energy) analysis
Five energy storage functions (ESM)
Multiple analyses to support the energy storage functions

## Slide 13: In-rush current analysis
In-rush current analysis compares the in-rush current requirements of loads with the capability of the generator sets or other sources to provide the in-rush current while maintaining interface standards
  Equipment in-rush current requirements detailed in load list
Equipment with large in-rush current
  Large transformers
  Induction motors
  Solenoid valves
  Equipment with large input filter capacitors
Study cases
  Many loads with large inrush come online at the same time
    Dark ship recovery
    Dead ship recovery
  A load with large inrush current during shift in operating mode
In-rush current remediation technologies

## Slide 14: Pulsed load analysis
Examines ability of power system to support pulsed loads without impacting power quality to other loads
EPS CONOPS describes the intended ways for the power system to be operated to support pulsed loads
  Subject pulse directly to the generator sets
  Use energy storage to reduce impact on generator sets
  Redirect power (when available) from other loads (such as propulsion)
EPLA provides an understanding of the other loads expected to be online and functional
Analysis should confirm
  Power quality is maintained throughout the power system
  Generator sets and other power system equipment are operated within their specification
  The fault protection system has the capability of discriminating between the pulse and a fault
U.S. Navy Railgun Test
(US Navy Photo)

## Slide 15: Quality of service analysis
Computes t1 and t2
  Reconfiguration time (t1)
  Generator start time (t2)
Assigns QOS category to all loads
  Uninterruptible
  Short term interrupt
  Long term interrupt
Evaluates if Mean Time Between Service Interruption (MTBSI) requirements met
  Requires estimating reliability properties of power system equipment
  Redundancy (or lack thereof) can identify critical components to concentrate data collection efforts on

## Slide 16: Endurance fuel calculations
Primary purpose is to determine the size of the fuel tanks
Endurance specified as one or more endurance set of metrics
  Economical Transit
    Economical transit distance and Endurance Speed
  Surge to Theater
    Surge to theater distance and Sustained Speed
  Operational Presence
    Operational mission
    Speed – Time Profile
    Operational Presence Time
Requires calculation of 24-hour average load for the applicable endurance set of metrics
  Typically uses load factor analysis
  May use parametric equation in early design stages
USS Donald Cook (DDG 75) USNS Laramie (T-AO 203)
(US Navy Photo)

## Slide 17: Annual energy usage and annual energy cost calculations
EPLA provides estimates for 24-hour averages for the different operational conditions.
  When coupled with propulsion power requirements, used to estimate annual fuel consumption.
Annual fuel consumption used for
  Determining whether ship meets energy efficiency requirements
  Provide a basis for estimating the cost of fuel over the ship’s service life
  Evaluate whether the shore-side and replenishment fleet refueling capacity is sufficient (naval ships)
USNS Earl Warren (T-AO 207)
(US Navy Photo)

## Slide 18: Proxy Load
A proxy load is used to represent a load or group of loads
Uses of proxy load
  Specific equipment may not be selected; proxy load provides an estimate of the load characteristics while not necessarily being derived from specific equipment.
  Data is not available for selected equipment; the proxy load could have characteristics of similar, but not identical equipment for which the data is available.
  Properties of loads or groups of load are parametrically estimated and assigned to the proxy load.
  Lumping together multiple smaller loads that have the same connection to the power system. (electrical lighting and electrical heaters for example).
  Combining loads that depend on each other, or are exclusive to each other; managing the interdependency with a proxy load may be convenient.
  Combining many loads, whether defined or not, that have the same connection to the power system for the purpose of simplifying system models; this technique is useful for load flow analysis, endurance fuel calculations, and annual fuel calculations.
Proxy loads should clearly identify the equipment or types of equipment they contain.
  If the proxy load includes a group of equipment, members of the group should be identified and the estimated characteristics for those members identified.
Electric Heater
USS Wisconsin (BB 64)
(Photo by Norbert Doerry)

## Slide 19: EPLA Evolution
In earliest stages of design, virtually all the loads in the load list are likely to be proxy loads.
  For each load, the load list may only estimate the connected
  Load factors based on default values
As the design matures, update the load list
  Add additional information to loads as needed by analysis
    Concentrate on the largest 50 to 100 loads
  Remove from proxy loads and model separately, loads that are defined
    Adjust (or eliminate) the proxy loads to reflect the load removal
Model the loads using one or more of the modeling techniques
  May employ proxy loads to group multiple loads from load list
During detail design and construction
  Replace all proxy loads in the load list with actual loads
  Improve the load models
During sea trials and ship operations
  Instrument loads (preferably the 50 – 100 largest loads) to update load models