## Slide 1: Load Lists Revision of 20 February 2026
Dr. Norbert Doerry
http://doerry.org/norbert/MarineElectricalPowerSystems/index.htm
© 2026 by Norbert Doerry This work is licensed via: CC BY 4.0 (https://creativecommons.org/)

## Slide 2: Essential Questions
What is a Load List and what is it used for? | Understand
How does one develop a load list? | Apply
How does one determine which data must be gathered? | Apply
How does one gather and manage the data? | Apply
How does one adjust a load list from a parent design? | Apply

## Slide 3: Introduction Load Lists
Tracks all electrical loads onboard the ship
  Configuration managed.
  Includes characteristics of the electrical loads necessary to create load models.
Should be complete
  All loads should be represented by an entry in the load list.
  Known loads with mostly known characteristics incorporated directly.
  Loads with significant uncertainty modeled as proxy loads.
T9070-A3-DPC-010/310-1
(DPC 310-1)
(formerly DDS 310-1)

## Slide 4: Proxy Loads
Represent a load or group of loads
  In early stages of design, actual equipment hasn’t been determined yet.
  Proxies serve as placeholders for equipment that hasn’t been defined.
  Characteristics based on parametric equations, similar equipment, or scaled equipment from other ships.
    Use an appropriate scaling relationship if scaling from another ship
  If representing a group of loads, all the loads should connect to the power system at the same points.
    Commonly done for electrical lighting and electric heaters
Proxy load definition
  Should clearly state what loads are part of the proxy load.
  Where possible, should identify estimated characteristics of constituent loads as well as the total proxy load roll-up.
Proxy load evolution
  As the design matures, constituent loads of the proxy load are removed from the proxy load and become defined loads in the load list.
    Proxy load characteristics are adjusted by removing the impact of the loads removed from the proxy load on the total proxy load roll-up.
  In detail design, as equipment becomes defined, all proxy loads should be replaced with defined loads.

## Slide 5: Sources of data
Master equipment list
Mission systems description and one line diagram
Electrical plant description and one line diagram
Distributed system descriptions and one-line diagrams
General/machinery arrangements
Product model (if it exists)
Discussions with system designers (if possible)
EPLAs of similar ships (if available)

## Slide 6: Data Elements
Nomenclature
Product breakdown structure identifier
Location on the ship (zone and/or compartment)
Point(s) of connection to the power system (power panel, load center, switchboard).
Identification Plate (nameplate) rating (include units)
Connected load (kW and kVAR)
Peak load (kW and kVAR)
Power type (voltage, number of phases, frequency)
Load behavior
Use during different ship operating conditions
Correlation with other loads
In-rush current demand (if applicable)
Temperature dependence (if any)
Tolerance to power interruptions (for QOS analysis – if applicable)
Load shed priority (mission priority)
References

## Slide 7: Data Elements (continued)
Nomenclature
  Descriptive name of a load
  Identical equipment should have the same base name followed by a unique identifier (Diesel Generator Set 1, Diesel Generator Set 2)
Product breakdown structure identifier
  Used to group loads in an understandable manner (i.e. SWBS)
Location on the ship (zone and/or compartment)
  Used to ensure the connection to the power system makes sense
Point(s) of connection to the power system (power panel, load center, switchboard).
  Early on, may only know the switchboard connection
  As the power distribution system is defined, the connection should be to the appropriate load center (and power panel)
  Loads with multiple points of connection should indicate the normal and alternate points of connection.
Product breakdown structure in
IEEE Std 45.1

## Slide 8: Data Elements (continued)
Identification Plate (nameplate) rating (include units)
  Nameplate may have rated load in amps or mechanical hp
Connected load (kW and kVAR)
  Nameplate rating converted to electrical real and reactive power (for ac systems)
Peak load (kW and kVAR)
  The maximum load expected in operation
  Often less than the connected load
    For example: motors driving a pump
Power type (voltage, number of phases, frequency)

## Slide 9: Data Elements (continued)
Load behavior
  Constant: When on, load does not deviate substantially from its average value.
  Multi-mode: When on, load has multiple modes, but the load does not change much while in a particular mode.
  Pulsed: When on, load is a pulsed load.
  Cyclic: When on, load is at its peak load for approximately a specified time, then off for approximately another specified time.
  Other: When on, load characteristics are other than one of the above options.
  Unknown: Load characteristics are unknown. More data gathering is required to develop a load model.
Use during different ship operating conditions
  For each of the operating conditions, an indicator (typically TRUE, FALSE, GROUP, or UNKNOWN) if the load is on.
  If GROUP, part of a group of loads, see Correlation with Other Loads.
  If UNKNOWN, additional data gathering is required before the load is modeled.
Electric Heater
USS Wisconsin BB-64
Photo by Norbert Doerry

## Slide 10: Data Elements (continued)
Correlation with other loads
  Provide information with respect to how this load relates to other loads.
  Possibly separately define groups of loads.
    This field lists groups that the load is a member of
    Rules for use of loads within a group part of group definition
In-rush current demand (if applicable)
  Amount of in-rush current.
  Alternately, a multiplier for the rated current.
  Should also have an indicator that the load has an in-rush current, but its magnitude is not known.
Boat Davit Winch
USS Wisconsin BB-64
Photo by Norbert Doerry

## Slide 11: Data Elements (continued)
Temperature dependence (if any)
  Indicates if load depends on the ambient condition
  TRUE, FALSE, UNKNOWN
  Electric heaters typically temperature dependent
Tolerance to power interruptions
  Longest power disruption that can be tolerated
  Example levels
    0 ms
    10 ms
    80 ms
    0.5 ms
    2 s
    2 m
    5 m
    Unknown
  Used to determine Quality of Service category
Electric Heater
USS Wisconsin BB-64
Photo by Norbert Doerry

## Slide 12: Data Elements (continued)
Load shed priority (mission priority)
  At a minimum should indicate if an emergency load
  Depends on mission priority load shed approach
    Traditional naval combatant approach
      Vital
      Semi-vital
      Non-vital
    Dynamic mission priority load shedding enables defining different priority levels for different operational conditions
References
  Each data element should reference one or more data sources
  Method of obtaining the reference (such as hypertext link) should be provided
Harpoon Missiles
USS Wisconsin BB-64
Photo by Norbert Doerry

## Slide 13: Managing the load list
Early in concept design
  May be managed as part of a ship synthesis software tool
  Extensive use of proxy loads
As design matures
  Spreadsheets may be employed
  Concentrate on obtaining credible data for 50 to 100 largest loads
    Usually accounts for 60% to 80% of the ship’s total load
In preliminary design
  Databases often used
  Usually requires at least one dedicated engineer
    Track down missing data
      Considerable interaction with potential vendors
      Considerable interaction with design team
    Replace proxy loads with actual loads where possible
    Develop credible estimates