## Slide 1: Power Electronics Capacity Sizing Electric Power Load Analysis (EPLA) Revision of 25 April 2026
Dr. Norbert Doerry
http://doerry.org/norbert/MarineElectricalPowerSystems/index.htm
© 2026 by Norbert Doerry This work is licensed via: CC BY 4.0 (https://creativecommons.org/)

## Slide 2: Essential Questions
How do the overload capabilities of power electronic converters differ from electromagnetic based generators? | Understand
What are the implications of the overload capabilities of power electronic converters? | Understand
What are the requirements for power electronic converter capacity? | Understand
What other considerations are there for selecting the capacity of power electronic converters? | Understand

## Slide 3: Introduction
Power electronic converters may be employed to connect two power systems having different power quality attributes (voltage, frequency, etc.)
Power electronic converters may have multiple inputs and multiple outputs
  IPMC (MIL-PRF-32272)
Power electronic converters generally have limited overload capability as compared to transformers and synchronous generators
  Commercial inverter
    2 x current rating for 3 seconds
    1.6 x current rating for 10 seconds
  MIL-DTL-3124 synchronous generator
    I2t ≥180 (7.75 x current rating for 3 seconds, 4.24 x current rating for 10 seconds)
    Overload rating: 1.5 times rated current for 2 minutes.

## Slide 4: ABS Rules for Building and Classing Marine Vessels
“Where transformers and/or converters form a part of the vessel’s electrical system supplying to essential services and services necessary for minimum comfortable conditions of habitability, as defined in 4-8-1/7.3.3 and 4-8-1/7.3.4, the number and capacity of the transformers and/or converters is to be such that, with any one transformer or converter, or any one single phase of a transformer, out of service, the remaining transformers and/or converters or remaining phases of the transformer are capable of supplying power to these loads under normal seagoing conditions.”
“Semiconductor converters are to be rated for continuous load conditions and if required by the application, are to have specified overload capabilities.”

## Slide 5: Load analysis
Traditional load analysis
  Assumes many loads where variation of the total load around the mean is small.
  Usually applicable at the total ship level
  Power electronic converters usually only serve a subset of the total load
    The variation of the total load around the mean is relatively larger
    Limited overload capability of power electronic converters may result in converters shutting down due to large cycling loads
Zonal load factor method (DPC 310-1)
  Zonal load factors account for variability in the total load due to having non-constant power loads
  Almost always results in a larger operating load as compared to the traditional load analysis
  Reduces risk of converters shutting down due to large cycling loads.

## Slide 6: Margin and service life allowance
Margin accounts for uncertainty in the operating load estimate during design and construction
  IEEE Std 45.1 recommendation
    Detail Design Margin: 5% for existing follow-on designs to 20% for new first-time designs
    Construction Margin: 5% for existing follow-on designs to 20% for new first-time designs
Service life allowance (SLA) accounts for growth in load while the ship is in-service
  IEEE Std 45.1 recommendation
    20% (1% per year for 20 years)

## Slide 7: Quality of service and survivability
Failure rates of power electronic converters are likely to be high enough to require redundancy
  Redundancy at the total converter level
    Requires one additional converter and system connectivity so all loads can be supplied with any one converter out of service.
  Redundancy of modules within the converter
    Requires being able to serve all loads with one module out of service
    Single points of failure must be sufficiently reliable
    Hot swapping capability is desirable
Power electronic converter ratings should be sufficient for both normal operation and cases where load is transferred from other power electronic converters
  May require load shedding
  Must have adequate overload capability for period of time it takes to shed loads

## Slide 8: In-rush current
Power electronic converters should be capable of providing sufficient in-rush current to connected loads.
  Electromagnetic-based loads such as transformers, motors, solenoids, and relays.
  Input capacitors
If power electronic converter unable to provide sufficient in-rush current, several mitigation strategies are possible
  Use starting resistor to limit the in-rush current; bypass resistor when in-rush transient is complete
  Soft start the converter (ramp up voltage slowly)
  Use low-voltage protection (LVP) controllers for non-vital loads.
    Requires manual restart after a loss of power
  For loads with input contactors, use a random delay between when power is applied to the load when the input contactors are closed.
  Use pre-charge circuitry
  Use power electronic converters with sufficient capacity to supply in-rush current

## Slide 9: Fault protection
Power electronic converters may not provide sufficient fault current to enable traditional coordination of circuit breakers
Alternate strategies
  Flatten the distribution system by using multiple output converters
    Output converter acts as one layer of circuit protection
    Only one circuit breaker between load and converter
  Use differential protection relay
    Subdivide distribution into protection zones
    Measure currents on all conductors at the boundary of the protection zones
    Use Kirchhoff’s current law (sum of currents should be zero) to determine which protection zone is zero
  Increase power rating of the power electronic converter until it has sufficient fault current capability to selectively trip circuit breakers

## Slide 10: Efficiency
Power electronic converter losses typically have a constant, no-load component and a component proportional to the load current squared.
If multiple modules are used to achieve power rating consider having the control system turn off modules when the load is low.
  Eliminate no-load component of losses
  Losses due to load current may rise

## Slide 11: Black start
Black start is energizing an electrical system after loss of power.
  Dark ship – All generator sets are offline, but energy storage is available for control systems and to enable startup.
  Dead ship – All generator sets are offline, and all energy storage is depleted (except for dedicated energy storage for emergency generator starting).
Starting a power electronic converter from either dark ship or dead ship may be impeded if the converter depends on cooling water that is powered by the converter.
  Consider employing a power electronic converter that has a reduced power rating when the cooling water is not available.
  Goal is for rating without cooling water to be sufficient to enable startup.