## Slide 1: Transformer Capacity Sizing Electric Power Load Analysis (EPLA) Revision of 2 May 2026
Dr. Norbert Doerry
http://doerry.org/norbert/MarineElectricalPowerSystems/index.htm
© 2026 by Norbert Doerry This work is licensed via: CC BY 4.0 (https://creativecommons.org/)

## Slide 2: Essential Questions
What is the procedure for determining transformer capacity? | Understand
What are the trade-offs with respect to using a single three-phase transformer and using three single-phase transformers | Understand
What options are available for addressing large transformer inrush current? | Understand
What other considerations are there for selecting the capacity of transformers? | Understand

## Slide 3: Introduction
Power transformers may be employed to connect two ac power systems the same frequency and potentially different voltages
Three phase power transformers may be composed of:
  Three single phase transformers
  One three-phase shell-type transformer
  One three-phase core-type transformer
Sources of requirements and recommendations
  46 CFR 111
  ABS Rules for Building and Classing Marine Vessels
  IEEE Std. 45.1, IEEE Recommended Practice for Electrical Installations on Shipboard - Design

## Slide 4: Load analysis
Traditional load analysis
  Assumes many loads where variation of the total load around the mean is small.
  Usually applicable at the total ship level
  Transformers usually only serve a subset of the total load
    The variation of the total load around the mean is relatively larger
    Extended periods of time in an overload may result in insulation damage within the transformer
Zonal load factor method (DPC 310-1)
  Zonal load factors account for variability in the total load due to having non- constant power loads
  Almost always results in a larger operating load as compared to the traditional load analysis
  Reduces risk of overloading transformers

## Slide 5: Margin and service life allowance
Margin accounts for uncertainty in the operating load estimate during design and construction
  IEEE Std 45.1 recommendation
    Detail Design Margin: 5% for existing follow-on designs to 20% for new first-time designs
    Construction Margin: 5% for existing follow-on designs to 20% for new first-time designs
  Service life allowance (SLA) accounts for growth in load while the ship is in-service
    IEEE Std 45.1 recommendation
      20% (1% per year for 20 years)

## Slide 6: Harmonic and common mode currents
Harmonic and common mode currents create heat within the transformer
  Currents do not contribute to useful work
  Common mode currents of most concern if the transformer has a delta primary and a wye secondary with the neutral connected to ground via a neutral grounding resistor
    Current through the neutral connection results in a circulating current in the primary windings
IEEE Std. 45.1 provides recommendations for derating transformers to account for additional heating

## Slide 7: Survivability
Ratings of transformers should account for …
  Normal operation
  Additional load applied via bus transfers when other transformers not in service
    May require load shedding
Delta-Delta transformers may be constructed from three single phase transformers
  Enables continued operation with the removal of one transformer
    Open delta configuration
    Capacity drops to about 58% of the full three transformer rating

## Slide 8: In-rush current
Large transformers may have a higher in-rush current than can be supplied by the generator sets
Options to address include:
  Use of pre-charge circuitry
  Replace one large transformer with multiple smaller transformers
    Do not energize multiple transformers at the same time

## Slide 9: Fault protection
Larger transformers have lower impedance
  Ensures secondary voltage is not too low at full power
  Low impedance results in higher fault currents on the secondary
    May exceed interrupting capability of circuit breakers on the secondary distribution system
Possible solution
  Replace one large transformer with multiple smaller transformers

## Slide 10: DC current saturation
If a transformer is a delta wye, with the neutral connected to ground via a neutral-grounding resistor ….
  If the distribution system on the secondary feeds an un-isolated rectifier that suffers a ground fault on the dc side …
  Then the transformer windings will experience a dc current component
A dc current component may result in transformer saturation if the transformer …
  Is fabricated using multiple single phase transformers
  Is fabricated using a shell-type transformer core
Transformers fabricated using a core-type transformer core are less susceptible to saturation from dc currents.