## Slide 1: Paralleling DC Power Supplies with Droop
Dr. Norbert Doerry and Dr. John V. Amy Jr.
December 11, 2025
http://doerry.org/norbert/MarineElectricalPowerSystems/index.htm
© 2025 by Norbert Doerry and John Amy This work is licensed via: CC BY 4.0 (https://creativecommons.org/)

## Slide 2: Introduction
Droop is a technique for allowing two power supplies to share power when paralleled.
Each power supply has a steady state characteristic where the voltage it regulates to is a function of either the power or current.
  Normally the relationship is linear: the voltage decreases as load increases
  If current is used, the droop characteristic is equivalent to a resistor.
With a linear droop, the droop characteristic is often specified in terms of a percentage drop in voltage (referenced to the nominal no load voltage) at full load.

## Slide 3: Current based Droop for two dc sources
Each supply is modeled by a no-load (open circuit) voltage and a droop resistance.
  In real power supplies, the droop resistance is virtual – no physical resistor is needed.
  Droop % =
  Each source is assumed to prevent reverse power (such as using a series diode)
The supply currents I1 and I2 must be non-negative.
  Sources have unidirectional power flow
  If then I2 = 0,
  If then I1 = 0,
If both I1 and I2 are non-negative
  , ,

## Slide 4: Equal No Load Voltages and Resistances Vary the Load
Set
Set
RL | VL | I1 | I2 | IL
Ohm | Volts | Amps | Amps | Amps
10 | 9.52 | 0.48 | 0.48 | 0.95
5 | 9.09 | 0.91 | 0.91 | 1.82
3.3 | 8.68 | 1.32 | 1.32 | 2.63
2.5 | 8.33 | 1.67 | 1.67 | 3.33
Equal sharing for all loads
, ,

## Slide 5: Equal No Load Voltages, Unequal Resistances Vary the Load
Set
Set
RL | VL | I1 | I2 | IL
Ohm | Volts | Amps | Amps | Amps
10 | 9.68 | 0.65 | 0.32 | 0.97
5 | 9.38 | 1.25 | 0.63 | 1.88
3.3 | 9.08 | 1.83 | 0.92 | 2.75
2.5 | 8.82 | 2.35 | 1.18 | 3.53
Same sharing fraction for all loads
, ,

## Slide 6: Unequal No Load Voltages, Equal Resistances Vary the Load
Set
Set
RL | VL | I1 | I2 | IL
Ohm | Volts | Amps | Amps | Amps
10 | 10.00 | 0.00 | 1.00 | 1.00
5 | 9.55 | 0.45 | 1.45 | 1.91
3.3 | 9.12 | 0.88 | 1.88 | 2.76
2.5 | 8.75 | 1.25 | 2.25 | 3.50
Increasing the voltage of one source creates an offset in current provided
, ,

## Slide 7: Unequal No Load Voltages (Auctioneering), Equal Resistances, Vary the Load
Set
Set
RL | VL | I1 | I2 | IL
Ohm | Volts | Amps | Amps | Amps
10 | 9.09 | 0.91 | 0.00 | 0.91
5 | 8.33 | 1.67 | 0.00 | 1.67
3.3 | 7.82 | 2.18 | 0.18 | 2.37
2.5 | 7.50 | 2.50 | 0.50 | 3.00
If voltage sources are significantly different, the lower voltage source will only contribute at high power levels.
Alternately, if at lower power levels, the lower voltage source will only contribute if the higher voltage source drops offline.
, ,

## Slide 8: Peak Shaving (Energy Storage) Example
Set
Set
RL | VL | I1 | I2 | IL
Ohm | Volts | Amps | Amps | Amps
10 | 9.09 | 0.91 | 0.00 | 0.91
5 | 8.33 | 1.67 | 0.00 | 1.67
3.3 | 8.00 | 2.00 | 0.42 | 2.42
2.5 | 8.00 | 2.00 | 1.20 | 3.20
Minimum Load Voltage fixed, Load current for Source 1 limited
, ,

## Slide 9: Droop In AC Systems
Frequency droop as a function of real power
  As real power supplied by source increases, the frequency decreases
  Enables sharing of real power among multiple generators
Voltage droop as a function of current, apparent power, or reactive power
  As current, apparent power, or reactive power increases, voltage decreases
  Enables sharing of reactive power among multiple generators
    If current or apparent power is used, assumes the real power is shared appropriately.

## Slide 10: Wrap up