## Slide 1: Experiment 2
Delta-Delta Transformer – Ungrounded System Ground Fault
Dr. Norbert Doerry and Dr. John V. Amy Jr.
http://doerry.org/norbert/MarineElectricalPowerSystems/index.htm
© 2024 by Norbert Doerry and John Amy This work is licensed via: CC BY 4.0 (https://creativecommons.org/)

## Slide 2: Schematic
Cp = 2.2 µF
R = 1200 Ω
RL = 300 Ω Rlamp = 450 Ω
Common Mode Current Probe
Current Meter (all phases)
Voltage Meter (all phases)
Rlamp

## Slide 3: Experiment 2
Wye
Parasitic
Delta
Secondary - LL
Secondary - LN
Transformer line
Secondary - LG
Load line

## Slide 4: Simulation Model
20240810 experiment 2.asc
LTspice

## Slide 5: Line to Line and Line to Neutral Voltages Unchanged during ground fault
Ground Fault

## Slide 6: Neutral to ground voltage is negative line to ground voltage during a ground fault; After fault clears, may have dc offset
Ground Fault
Note: Ground Lamps not connected to ground

## Slide 7: Phase to Ground Voltages
Ground Fault
Trapped Charge on capacitors may result in dc offset
Note: Ground Lamps not connected to ground
During Fault, line to ground voltages equal line to line voltages

## Slide 8: Ground Lamps: faulted phase light is out, others bright during ground fault
Ground Fault
Lamp resistance dissipates trapped charge in parasitic capacitors

## Slide 9: Ground Fault Currents (Common Mode)
The neutral resistors and load resistors do not contribute to ground current
The current through the capacitors are
Common Mode Equivalent Circuit

## Slide 10: Common Mode Currents to ground
Ground Fault
Without Ground Lamps
With Ground Lamps

## Slide 11: Common Mode Equivalent circuit produces same results
With Ground Lamps

## Slide 12: Common Mode Currents in bus
Kirchhoff Current Law (KCL) implies Comm mode current out of transformer is zero
KCL also implies Common mode current into delta load resistors is zero

## Slide 13: Wrap Up