## Slide 1: Experiment 6
Delta-Wye Transformer – 4 wire - Ungrounded System Unbalanced Load
Dr. Norbert Doerry and Dr. John V. Amy Jr.
http://doerry.org/norbert/MarineElectricalPowerSystems/index.htm
© 2024 by Norbert Doerry and John Amy This work is licensed via: CC BY 4.0 (https://creativecommons.org/)

## Slide 2: Schematic
Cp = 2.2 µF
R = 1200 Ω
RL = 300 Ω
RLa = 200 Ω Rlamp = 450 Ω
N = 5.2
Common Mode Current Probe
Current Meter (all phases)
Voltage Meter (all phases)
Rlamp
(Neglecting losses)

## Slide 3: Experiment 6
Wye
Parasitic
Wye-Load
Secondary - LL
Secondary - LN
Primary line
Secondary - LG
Load line
Secondary line

## Slide 4: Simulation Model
20240831 experiment 6.asc
LTspice

## Slide 5: Steady State Voltages
Primary Line to Line Voltage: Peak = 294 volts
Secondary Line to Line Voltage: Peak = 98 V volts

## Slide 6: Line currents into the wye load and into primary not balanced with unbalanced load
Balanced Load Unbalanced Load
Current into
Wye load
Current into
Primary
Circuit
Protection
on Primary may not trip with overload of a single conductor on secondary

## Slide 7: Unbalanced load results in current in the Neutral Conductor
Balanced Load Unbalanced Load
=94.3 mA peak

## Slide 8: Unbalanced load results in circulating current in the delta windings
Balanced Load Unbalanced Load
.0 mA peak

## Slide 9: Unbalanced load results in unbalanced current into the primary windings
Balanced Load Unbalanced Load

## Slide 10: No neutral to ground voltage (CM Voltage) or CM Current through Parasitic Capacitances or lamp resistances
Balanced Load Unbalanced Load
Neutral to Ground Voltage
CM Current through Parasitic Capacitances and Lamp Resistors

## Slide 11: Wrap Up